## String Length Calculator
Your title here….. | [13 empty] | 600 | 2 | TS480 | 8000 | 0.98 | 200
|  |  | Key |  | Scale | [8 empty] | 1000 | 4 | TS208 | 5750 | 0.975 | 200
|  |  | User Input |  |  |  |  | Min Vmppt |  |  | Min Temp Voc
|  |  | Listed choices |  |  |  | <100% | 100-110% | >110% | <90% | 90-100% | >100%
[5 empty] | Voltage Scale |  | <-------¦ | <--------------> | ¦<------------- | ------------->¦ | <-------------> | ¦--------->
[8 empty] | Low | Great |  | Be careful | NEC no go…
Module Input Data
Module Name | Boviet 250W Poly | <<<< |  |  |  |  | <80% | 80-90% | 90-125% | 125-150% | >150%
V Temp Coeff (%) | -0.33% |  |  |  | Power Scale |  | <-------¦ | <--------------> | <--------------> | <--------------> | ¦--------->
Module Power (STC, W) | 250 | [5 empty] | Ok, but underpowered…. |  | Great
Voc (V) | 37.5
Vmppt (V) | 30.2 |  |  | Notes
Imppt (A) | 8.28 |  |  | > Should not exceed Min Temp Voc maximum voltage (either 600 or 1,000V)
Cell T Rise (°C) | 20 |  |  | > Change String Length Input Cell to be under Min-Temp Voc limit, make sure inverter power level and other parameters look good
(Note Min Vmppt is 425V: Above this unit will give full power, but unit will still track down to 200V or below)
String Length Input | 18
System |  |  |  | TrueString String Length Calculator
Max Voc (V) | 1000
[5 empty] | String Length: | 15 | 16 | 17 | 18 | 19 | 20 | 21
Ambient Temperature Assumptions |  |  |  | Min Temp | Voc (V) | 627.4688 | 669.3 | 711.1312 | 752.9625 | 794.7937 | 836.625 | 878.4562 | V
Min Temp (°C) | -10 |  |  | Min Temp | Vmppt (V) | 475.4235 | 507.1184 | 538.8133 | 570.5082 | 602.2031 | 633.898 | 665.5929 | V
Max Temp (°C) | 62 |  |  |  | Pdc (W) | 7873.0132 | 8397.8807 | 8922.7482 | 9447.6158 | 9972.4833 | 10497.3509 | 11022.2184 | W
Nominal Temp (°C) | 25 |  |  |  | Pac (W) | 7715.5529 | 8229.9231 | 8744.2933 | 9258.6635 | 9773.0337 | 10287.4039 | 10801.7741 | W
|  |  |  | Nom Temp | Vmppt (V) | 423.102 | 451.3088 | 479.5156 | 507.7224 | 535.9292 | 564.136 | 592.3428 | V
TrueString Inverter Input Data |  |  |  |  | Pdc (W) | 7006.5691 | 7473.6737 | 7940.7783 | 8407.8829 | 8874.9876 | 9342.0922 | 9809.1968 | W
Model | TS480 |  |  |  | Pac (W) | 6866.4377 | 7324.2003 | 7781.9628 | 8239.7253 | 8697.4878 | 9155.2503 | 9613.0128 | W
Power Rating (W) | 8000 |  |  | Max Temp | Vmppt (V) | 367.7907 | 392.3101 | 416.8295 | 441.3488 | 465.8682 | 490.3876 | 514.907 | V
Average Efficiency (%) | 98% |  |  |  | Pdc (W) | 6090.614 | 6496.6549 | 6902.6959 | 7308.7368 | 7714.7777 | 8120.8187 | 8526.8596 | W
# Strings | 2 |  |  |  | Pac (W) | 5968.8017 | 6366.7218 | 6764.6419 | 7162.5621 | 7560.4822 | 7958.4023 | 8356.3224 | W
Min Vmppt (V) | 200 |  |  | STC Stacking Ratio |  | 93.75% | 100% | 106.2% | 112.5% | 118.8% | 125% | 131.2%
HiQ Solar, Inc. v4.1, March 2017 |  |  |  | Use at own risk, HiQ Solar, Inc. accepts no responsibility for errors, omissions, etc.
www.hiqsolar.com | [12 empty] | Rugged Solar Inverters for Commercial 3-Phase Installations
Note on G5: Scale of % Vmppt to % Voc range
Note on C8: Guy Foster: Dropdown, driven from "Module Table" tab
Note on G9: Power scale compared to inverter nominal output power
Note on B14: Usually difference between Normal Cell Operating Temperature (NOCT) and STC temperature
Note on F18: Calculations are based on STC. Temperature derating applied to voltage but not current values. Powers calculated from Vmppt (temp derated) and Imp (not derated). Tool gives order of magnitude guidance but is not a substitute for a system design tool.
Note on B28: Input cells populated with correct info for HiQ Solar TrueString inverter
Note on F31: STC module power vs. inverter nominal power rating

## Your Module Table
Module Name | Model # | V Temp Coeff (%) | Module Power (STC, W) | Voc (V) | Vmppt (V) | Imppt (A) | Cell T Rise (°C)
Astronergy 250W | CHSM6610P-250 | -0.31% | 250 | 38.19 | 30.3 | 8.27 | 20 | 'Vlookup' list that drives "Dropdown Master" tab.
Astronergy 255W | CHSM6610P-255 | -0.31% | 255 | 38.4 | 30.68 | 8.33 | 20 | Feel free to add your own modules to the list as needed
Astronergy 260W | CHSM6610P-260 | -0.31% | 260 | 38.53 | 31.05 | 8.39 | 20
Astronergy 265W | CHSM6610P-265 | -0.31% | 265 | 38.72 | 31.43 | 8.46 | 20
Astronergy 270W | CHSM6610P-270 | -0.31% | 270 | 38.91 | 31.78 | 8.52 | 20
Astronergy 300W | CHSM6612P-300 | -0.311% | 300 | 45.16 | 35.74 | 8.4 | 20
Astronergy 305W | CHSM6612P-305 | -0.311% | 305 | 45.29 | 35.77 | 8.53 | 20
Astronergy 310W | CHSM6612P-310 | -0.311% | 310 | 45.42 | 35.8 | 8.68 | 20
Astronergy 315W | CHSM6612P-315 | -0.311% | 315 | 45.55 | 35.83 | 8.8 | 20
Astronergy 320W | CHSM6612P-320 | -0.311% | 320 | 45.68 | 35.86 | 8.93 | 20
BenQ 96 cell 333W | PM096B00 | -0.26% | 333 | 64.9 | 54.7 | 6.09 | 20
Boviet 250W Poly | BVM6610P-250 | -0.33% | 250 | 37.5 | 30.2 | 8.28 | 20
Boviet 255W Poly | BVM6610P-255 | -0.33% | 255 | 37.7 | 30.4 | 8.39 | 20
Boviet 260W Poly | BVM6610P-260 | -0.33% | 260 | 37.9 | 30.6 | 8.5 | 20
Boviet 265W Poly | BVM6610P-265 | -0.33% | 265 | 38.1 | 30.8 | 8.61 | 20
Boviet 270W Poly | BVM6610P-270 | -0.33% | 270 | 38.3 | 31 | 8.71 | 20
Boviet 270W Mono | BVM6610M-270 | -0.35% | 270 | 38.1 | 31.3 | 8.64 | 20
Boviet 275W Mono | BVM6610M-275 | -0.35% | 275 | 38.6 | 31.5 | 8.74 | 20
Boviet 280W Mono | BVM6610M-280 | -0.35% | 280 | 38.9 | 31.7 | 8.82 | 20
Boviet 285W Mono | BVM6610M-285 | -0.35% | 285 | 39.2 | 31.8 | 8.97 | 20
Boviet 315W Poly | BVM6612P-315 | -0.33% | 315 | 45.3 | 36.8 | 8.56 | 20
Boviet 320W Poly | BVM6612P-320 | -0.33% | 320 | 45.5 | 37 | 8.65 | 20
Boviet 325W Poly | BVM6612P-325 | -0.33% | 325 | 45.7 | 37.2 | 8.74 | 20
Boviet 330W Poly | BVM6612P-330 | -0.33% | 330 | 45.8 | 37.4 | 8.83 | 20
Canadian Solar 250W | CS6P-250P | -0.34% | 250 | 37.2 | 30.1 | 8.3 | 20
Canadian Solar 255W | CS6P-255P | -0.34% | 255 | 37.4 | 30.2 | 8.43 | 20
Canadian Solar 260W | CS6P-260P | -0.34% | 260 | 37.5 | 30.4 | 8.56 | 20
Canadian Solar 270W | CS6K-270M | -0.31% | 270 | 38.2 | 31.1 | 8.67 | 20
Canadian Solar 275W | CS6K-275M | -0.31% | 275 | 38.3 | 31.3 | 8.8 | 20
Canadian Solar 280W | CS6X-280P | -0.34% | 280 | 44.2 | 35.6 | 7.86 | 20
Canadian Solar 295W | CS6X-295P | -0.34% | 295 | 44.5 | 36 | 8.19 | 20
Canadian Solar 310W | CS6X-305P | -0.34% | 310 | 44.9 | 36.4 | 8.52 | 20
Canadian Solar 315W | CS6X-315P | -0.34% | 315 | 45.1 | 36.6 | 8.61 | 20
Canadian Solar 325W | CS6X-325P | -0.31% | 325 | 45.5 | 37 | 8.78 | 20
Canadian Solar 340W | CS6U-340M | -0.31% | 340 | 46.2 | 37.9 | 8.97 | 20
ET Solar 290W | ET-P672305WW | -0.34% | 290 | 44.75 | 35.92 | 8.08 | 20
ET Solar 295W | ET-P672305WW | -0.34% | 295 | 44.78 | 36.17 | 8.16 | 20
ET Solar 300W | ET-P672305WW | -0.34% | 300 | 44.89 | 36.68 | 8.18 | 20
ET Solar 305W | ET-P672305WW | -0.34% | 305 | 45.12 | 37.18 | 8.21 | 20
Hanwha 290W | Q.PRO L 290 | -0.33% | 290 | 44.89 | 35.54 | 8.23 | 20
Hanwha 295W | Q.PRO L 295 | -0.33% | 295 | 45.1 | 35.69 | 8.33 | 20
Hanwha 300W | Q.PRO L 300 | -0.33% | 300 | 45.32 | 35.85 | 8.44 | 20
Hanwha 305W | Q.PRO L 305 | -0.33% | 305 | 45.53 | 36 | 8.54 | 20
Hanwha 310W | Q.PRO L 310 | -0.33% | 310 | 45.75 | 36.15 | 8.65 | 20
Hanwha 300W | HSL72P6-PA-4-300 | -0.33% | 300 | 45.5 | 36.5 | 8.22 | 20
Hanwha 300W | Q.PEAK-G4.1 300 | -0.28% | 300 | 39.76 | 32.41 | 9.26 | 20
Hanwha 305W | Q.PEAK-G4.1 305 | -0.28% | 305 | 40.05 | 32.62 | 9.35 | 20
Heliene 295W | 72M295 | -0.34% | 295 | 44.77 | 36.4 | 8.1 | 20
Heliene 300W | 72M300 | -0.34% | 300 | 44.96 | 36.55 | 8.2 | 20
Heliene 305W | 72M305 | -0.34% | 305 | 45.1 | 36.65 | 8.32 | 20
Heliene 300W | 72M310 | -0.34% | 310 | 45.4 | 36.77 | 8.43 | 20
Hyundai 300W | HiS-S300MI | -0.334% | 300 | 45.4 | 37.4 | 8 | 20
Hyundai 300W | HiS-M300TI | -0.32% | 300 | 44.9 | 35.8 | 8.4 | 20
Hyundai 305W | HiS-M305TI | -0.32% | 305 | 45.1 | 36 | 8.5 | 20
Hyundai 310W | HiS-M310TI | -0.32% | 310 | 45.3 | 36.1 | 8.6 | 20
Hyundai 325W | HiS-S325TI | -0.33% | 325 | 46.1 | 37.8 | 8.6 | 20
Hyundai 330W | HiS-S330TI | -0.33% | 330 | 46.3 | 38 | 8.7 | 20
Hyundai 335W | HiS-S335TI | -0.33% | 335 | 46.5 | 38.2 | 8.78 | 20
JA Solar 290W | JAP6 72-290/3BB | -0.33% | 290 | 45.72 | 36.39 | 7.97 | 20
JA Solar 295W | JAP6 72-295/3BB | -0.33% | 295 | 45.9 | 36.6 | 8.06 | 20
JA Solar 300W | JAP6 72-300/3BB | -0.33% | 300 | 46.08 | 36.82 | 8.15 | 20
JA Solar 305W | JAP6 72-305/3BB | -0.33% | 305 | 46.2 | 36.97 | 8.25 | 20
JA Solar 310W | JAP6 72-310/3BB | -0.33% | 310 | 46.3 | 37.04 | 8.37 | 20
Jinko Solar 250W | JKM250P | -0.31% | 250 | 37.7 | 30.5 | 8.2 | 20
Jinko Solar 255W | JKM255P | -0.31% | 255 | 38 | 30.8 | 8.28 | 20
Jinko Solar 260W | JKM260P | -0.31% | 260 | 38.1 | 31.1 | 8.37 | 20
Jinko Solar 265W | JKM265P | -0.31% | 265 | 38.6 | 31.4 | 8.44 | 20
Jinko Solar 270W | JKM270P | -0.31% | 270 | 38.8 | 31.7 | 8.52 | 20
Jinko Solar 300W | JKM300P | -0.31% | 300 | 45.3 | 36.6 | 8.2 | 20
Jinko Solar 305W | JKM305P | -0.31% | 305 | 45.6 | 36.8 | 8.3 | 20
Jinko Solar 310W | JKM310P | -0.31% | 310 | 45.9 | 37 | 8.38 | 20
Jinko Solar 315W | JKM315P | -0.31% | 315 | 46.2 | 37.2 | 8.48 | 20
Jinko Solar 320W | JKM320P | -0.31% | 320 | 46.4 | 37.4 | 8.56 | 20
Kyocera 260W | KU260-6MCA | -0.36% | 260 | 38.3 | 31 | 8.39 | 20
Kyocera 265W | KU265-6MCA | -0.36% | 265 | 38.3 | 31 | 8.55 | 20
Kyocera 320W | KD320GX-LFB | -0.36% | 320 | 49.5 | 40.1 | 7.99 | 20
Kyocera 325W | KD325GX-LFB | -0.36% | 325 | 49.7 | 40.3 | 8.07 | 20
LG 250W | LG250S1C-G3 | -0.343% | 250 | 37.6 | 29.8 | 8.39 | 20
LG 255W | LG255S1C-G3 | -0.343% | 255 | 37.7 | 30 | 8.5 | 20
LG 260W | LG260S1C-G3 | -0.343% | 260 | 37.9 | 30.2 | 8.61 | 20
LG 265W | LG265S1C-B3 | -0.31% | 265 | 38.3 | 31.3 | 8.49 | 20
LG 270W | LG270S1C-B3 | -0.31% | 270 | 38.5 | 31.5 | 8.58 | 20
LG 275W | LG275S1C-B3 | -0.31% | 275 | 38.7 | 31.7 | 8.68 | 20
LG 280W | LG280S1C-B3 | -0.31% | 280 | 38.8 | 31.9 | 8.78 | 20
LG 285W | LG285N1C | -0.31% | 285 | 39 | 31.6 | 9.09 | 20
LG 290W | LG290N1C | -0.31% | 290 | 39.2 | 31.8 | 9.19 | 20
LG 300W | LG300N1C-G4 | -0.28% | 300 | 39.8 | 32.2 | 9.34 | 20
LG 305W | LG305N1C-B3 | -0.29% | 305 | 40 | 32.1 | 9.52 | 20
LG 310W | LG310N1C-G4 | -0.28% | 310 | 40.4 | 32.8 | 9.45 | 20
LG 315W | LG315N1C-G4 | -0.28% | 315 | 40.6 | 33.2 | 9.5 | 20
LG 360W | LG360N2W-B3 | -0.28% | 360 | 48.3 | 38.4 | 9.39 | 20
LG 365W | LG365N2W-B3 | -0.28% | 365 | 48.4 | 38.6 | 9.46 | 20
LG 370W | LG370N2W-G4 | -0.28% | 370 | 48 | 39.2 | 9.44 | 20
Panasonic 325W | VBHN325SA16 | -0.25% | 325 | 69.6 | 57.6 | 5.65 | 20
Panasonic 330W | VBHN330SA16 | -0.25% | 330 | 69.7 | 58 | 5.7 | 20
REC 265W TP | REC265TP | -0.31% | 265 | 38.3 | 31.1 | 8.53 | 20
REC 270W TP | REC270TP | -0.31% | 270 | 38.6 | 31.2 | 8.66 | 20
REC 275W TP | REC275TP | -0.31% | 275 | 38.8 | 31.4 | 8.76 | 20
REC 280W TP | REC280TP | -0.31% | 280 | 39.2 | 31.9 | 8.78 | 20
REC 275W TP2 | REC275TP2 | -0.31% | 275 | 38.2 | 31.5 | 8.74 | 20
REC 280W TP2 | REC280TP2 | -0.31% | 280 | 38.4 | 31.7 | 8.84 | 20
REC 285W TP2 | REC285TP2 | -0.31% | 285 | 38.6 | 31.9 | 8.95 | 20
REC 290W TP2 | REC290TP2 | -0.31% | 290 | 38.8 | 32.1 | 9.05 | 20
REC 295W TP2 | REC295TP2 | -0.31% | 295 | 39 | 32.3 | 9.14 | 20
REC 330W TP2S | REC330TP2S72 | -0.31% | 330 | 46 | 38.1 | 8.67 | 20
REC 335W TP2S | REC335TP2S72 | -0.31% | 335 | 46.2 | 38.3 | 8.75 | 20
REC 340W TP2S | REC340TP2S72 | -0.31% | 340 | 46.3 | 38.5 | 8.84 | 20
REC 345W TP2S | REC345TP2S72 | -0.31% | 345 | 46.5 | 38.7 | 8.92 | 20
REC 350W TP2S | REC350TP2S72 | -0.31% | 350 | 46.7 | 38.9 | 9 | 20
RECOM Solar 235W Poly | RCM-235-6PB | -0.32% | 235 | 36.3 | 30 | 7.83 | 20
RECOM Solar 240W Poly | RCM-240-6PB | -0.32% | 240 | 36.9 | 30.1 | 8.05 | 20
RECOM Solar 245W Poly | RCM-245-6PB | -0.32% | 245 | 37 | 30.1 | 8.12 | 20
RECOM Solar 250W Poly | RCM-250-6PB | -0.32% | 250 | 37.1 | 30.2 | 8.35 | 20
RECOM Solar 255W Poly | RCM-255-6PB | -0.32% | 255 | 37.6 | 30.5 | 8.36 | 20
RECOM Solar 260W Poly | RCM-260-6PB | -0.32% | 260 | 38 | 30.8 | 8.47 | 20
RECOM Solar 265W Poly | RCM-265-6PB | -0.32% | 265 | 38.2 | 31.1 | 8.55 | 20
RECOM Solar 270W Poly | RCM-270-6PB | -0.32% | 270 | 38.6 | 31.4 | 8.63 | 20
RECOM Solar 280W Poly | RCM-280-6PB | -0.32% | 280 | 38.78 | 31.68 | 8.83 | 20
RECOM Solar 300W Poly | RCM-300-6PB | -0.32% | 300 | 44.8 | 36.6 | 8.2 | 20
RECOM Solar 305W Poly | RCM-305-6PB | -0.32% | 305 | 44.9 | 36.8 | 8.33 | 20
RECOM Solar 310W Poly | RCM-310-6PB | -0.32% | 310 | 45 | 37 | 8.42 | 20
RECOM Solar 315W Poly | RCM-315-6PB | -0.32% | 315 | 45.4 | 37.8 | 8.44 | 20
RECOM Solar 320W Poly | RCM-320-6PB | -0.32% | 320 | 45.94 | 38.23 | 8.46 | 20
RECOM Solar 325W Poly | RCM-325-6PB | -0.32% | 325 | 45.99 | 38.25 | 8.49 | 20
RECOM Solar 330W Poly | RCM-330-6PB | -0.32% | 330 | 46.2 | 38.77 | 8.51 | 20
RECOM Solar 335W Poly | RCM-335-6PB | -0.32% | 335 | 46.24 | 39.22 | 8.54 | 20
RECOM Solar 340W Poly | RCM-340-6PB | -0.32% | 340 | 46.29 | 39.71 | 8.56 | 20
RECOM Solar 310W Mono | RCM-310-6MA | -0.31% | 310 | 45.3 | 36.2 | 8.57 | 20
RECOM Solar 315W Mono | RCM-315-6MA | -0.31% | 315 | 45.7 | 36.6 | 8.63 | 20
RECOM Solar 320W Mono | RCM-320-6MA | -0.31% | 320 | 45.9 | 37 | 8.68 | 20
RECOM Solar 325W Mono | RCM-325-6MA | -0.31% | 325 | 46 | 37.3 | 8.72 | 20
RECOM Solar 330W Mono | RCM-330-6MA | -0.3% | 330 | 46.2 | 37.7 | 8.77 | 20
RECOM Solar 335W Mono | RCM-335-6MA | -0.3% | 335 | 46.4 | 37.9 | 8.85 | 20
RECOM Solar 340W Mono | RCM-340-6MA | -0.3% | 340 | 46.5 | 38 | 8.95 | 20
RECOM Solar 345W Mono | RCM-345-6MA | -0.3% | 345 | 46.6 | 38.1 | 9.06 | 20
RECOM Solar 350W Mono | RCM-350-6MA | -0.3% | 350 | 46.7 | 38.2 | 9.16 | 20
RECOM Solar 355W Mono | RCM-355-6MA | -0.3% | 355 | 46.8 | 38.3 | 9.27 | 20
Solaria 315W BX | PXT-315R-BX | -0.32% | 315 | 44.2 | 36.2 | 8.84 | 20
Solaria 320W BX | PXT-320R-BX | -0.32% | 320 | 44.2 | 36.2 | 8.84 | 20
Solaria 325W BX | PXT-325R-BX | -0.32% | 325 | 44.5 | 36.7 | 8.86 | 20
Solaria 325W WX | PXT-325R-WX | -0.32% | 325 | 44.3 | 36.4 | 8.93 | 20
Solaria 330W WX | PXT-330R-WX | -0.32% | 330 | 44.5 | 36.6 | 9.02 | 20
Solaria 390W WX | PXT-390C-WX | -0.32% | 390 | 41.2 | 33.6 | 8.52 | 20
Solaria 395W WX | PXT-395C-WX | -0.32% | 395 | 41.4 | 33.9 | 8.6 | 20
Solaria 400W WX | PXT-400C-WX | -0.32% | 400 | 41.6 | 34.1 | 8.6 | 20
SolarWorld 270W | SW270 Mono | -0.3% | 270 | 39.2 | 30.9 | 8.81 | 20
SolarWorld 285W | SW285 Mono | -0.3% | 285 | 39.7 | 31.3 | 9.2 | 20
SolarWorld 290W | SW290 Mono | -0.3% | 290 | 39.9 | 31.4 | 9.33 | 20
SolarWorld 295W | SW295 Mono | -0.3% | 295 | 40 | 31.5 | 9.45 | 20
SolarWorld 300W | SW300 Mono | -0.3% | 300 | 40.1 | 31.6 | 9.57 | 20
SolarWorld 340W | SW340 XL Mono | -0.304% | 340 | 47.6 | 38 | 9.01 | 20
SolarWorld 345W | SW345 XL Mono | -0.304% | 345 | 47.8 | 38.2 | 9.1 | 20
SolarWorld 350W | SW350 XL Mono | -0.304% | 350 | 48 | 38.4 | 9.17 | 20
Stion 150W | STL-150A (CIGS module) | -0.24% | 150 | 80.8 | 62.7 | 2.39 | 20
Suniva 275W | OPT275-60-4-1B0 | -0.335% | 275 | 38.6 | 31.5 | 8.74 | 20
Suniva 315W | OPT 315-72-4-100-B | -0.335% | 315 | 45.9 | 36.5 | 8.62 | 20
Suniva 320W | OPT 320-72-4-100-B | -0.335% | 320 | 46.1 | 36.8 | 8.69 | 20
Suniva 325W | OPT 325-72-4-100-BAA | -0.335% | 325 | 46.4 | 37.1 | 8.76 | 20
Suniva 330W | OPT 330-72-4-100 | -0.34% | 330 | 46.5 | 37.5 | 8.8 | 20
Suniva 340W | OPT 340-72-4-100-BAA | -0.335% | 340 | 46 | 37.8 | 8.99 | 20
SunPower E19 320W | SPR-E19-320 | -0.27% | 320 | 64.8 | 54.7 | 5.86 | 20
SunPower E20 327W | SPR-E20-327 | -0.27% | 327 | 64.9 | 54.7 | 5.98 | 20
SunPower P17 330W | SPR-P17-330-COM | -0.34% | 330 | 50.9 | 41.9 | 7.88 | 20
SunPower P17 335W | SPR-P17-335-COM | -0.34% | 335 | 51.1 | 42.2 | 7.94 | 20
SunPower P17 340W | SPR-P17-340-COM | -0.34% | 340 | 51.3 | 42.5 | 8 | 20
SunPower P17 345W | SPR-P17-345-COM | -0.34% | 345 | 51.5 | 42.8 | 8.06 | 20
SunPower P17 350W | SPR-P17-350-COM | -0.34% | 350 | 51.7 | 43.1 | 8.12 | 20
SunPower P17 355W | SPR-P17-355-COM | -0.34% | 355 | 51.9 | 43.4 | 8.18 | 20
SunPower X21 335W | SPR-X21-335-BLK | -0.25% | 335 | 67.9 | 57.3 | 5.85 | 20
SunPower X21 345W | SPR-X21-345 | -0.25% | 345 | 68.2 | 57.3 | 6.02 | 20
SunPower E19 410W | SPR-E19-410-COM | -0.275% | 410 | 85.3 | 72.9 | 5.62 | 20
SunPower E20 435W | SPR-E20-435-COM | -0.275% | 435 | 85.6 | 72.9 | 5.97 | 20
Sunpreme 290W Smart | Maxima GxB 290 SM | 0% | 290 | 38.6 | 33.7 | 8.6 | 20
Sunpreme 300W Smart | Maxima GxB 300 SM | 0% | 300 | 39.4 | 34.5 | 8.7 | 20
Sunpreme 310W Smart | Maxima GxB 310 SM | 0% | 310 | 39.5 | 35.2 | 8.8 | 20
Sunpreme 290W | Maxima GxB 290 | -0.21% | 290 | 43.9 | 33.7 | 8.6 | 20
Sunpreme 300W | Maxima GxB 300 | -0.21% | 300 | 44.9 | 34.5 | 8.7 | 20
Sunpreme 310W | Maxima GxB 310 | -0.21% | 310 | 45.9 | 35.2 | 8.8 | 20
Sunpreme 340W | Maxima GxB 340 | -0.27% | 340 | 51.4 | 41 | 8.3 | 20
Sunpreme 350W Smart | Maxima GxB 350 SM | 0% | 350 | 46.1 | 41.2 | 8.5 | 20
Sunpreme 360W Smart | Maxima GxB 360 SM | 0% | 360 | 46.8 | 41.9 | 8.6 | 20
Sunpreme 370W Smart | Maxima GxB 370 SM | 0% | 370 | 47.5 | 42.5 | 8.7 | 20
Sunpreme 350W | Maxima GxB 350 | -0.27% | 350 | 51.8 | 41.6 | 8.4 | 20
Sunpreme 360W | Maxima GxB 360 | -0.27% | 360 | 52.2 | 42.4 | 8.5 | 20
Sunpreme 370W | Maxima GxB 370 | -0.28% | 370 | 54.7 | 42.5 | 8.7 | 20
Sunpreme 490W | Maxima GxB 490 | -0.24% | 490 | 71.8 | 56.3 | 8.7 | 20
Sunpreme 500W | Maxima GxB 500 | -0.24% | 500 | 72.9 | 57.4 | 8.8 | 20
Sunpreme 510W | Maxima GxB 510 | -0.24% | 510 | 74.7 | 57.3 | 8.9 | 20
Trinasmart 250W | TSM-250-PC05A.082 | 0% | 250 | 33 | 30.3 | 8.27 | 20
Trinasmart 255W | TSM-255-PC05A.082 | 0% | 255 | 33 | 30.5 | 8.37 | 20
Trinasmart 260W | TSM-260-PC05A.082 | 0% | 260 | 33 | 30.6 | 8.5 | 20
Trinasmart 265W | TSM-265-PC05A.082 | 0% | 265 | 33 | 30.8 | 8.61 | 20
Trinasmart 260W | TSM-260-DC05A.052 | 0% | 260 | 33.4 | 30.7 | 8.49 | 20
Trinasmart 265W | TSM-265-DC05A.052 | 0% | 265 | 33.4 | 30.7 | 8.63 | 20
Trinasmart 270W | TSM-270-DC05A.082 | 0% | 270 | 33.4 | 30.8 | 8.77 | 20
Trinasmart 275W | TSM-275-DC05A.082 | 0% | 275 | 33.4 | 31.2 | 8.82 | 20
Trina 225W | TSM-225PA05 | -0.32% | 225 | 36.9 | 29.4 | 7.66 | 20
Trina 230W | TSM-230PA05 | -0.32% | 230 | 37 | 29.8 | 7.72 | 20
Trina 235W | TSM-235PA05 | -0.32% | 235 | 37.1 | 30.1 | 7.81 | 20
Trina 240W | TSM-240PA05 | -0.32% | 240 | 37.2 | 30.4 | 7.89 | 20
Trina 245W | TSM-245PA05 | -0.32% | 245 | 37.3 | 30.7 | 7.98 | 20
Trina 250W | TSM-250PA05 | -0.32% | 250 | 37.6 | 30.3 | 8.26 | 20
Trina 290W | TSM-290 PD14 | -0.33% | 290 | 44.9 | 36.1 | 8.04 | 20
Trina 295W | TSM-295 PD14 | -0.33% | 295 | 45.2 | 36.6 | 8.07 | 20
Trina 300W | TSM-300 PD14 | -0.33% | 300 | 45.3 | 36.9 | 8.13 | 20
Trina 305W | TSM-305 PD14 | -0.33% | 305 | 45.4 | 37 | 8.25 | 20
Trina 310W | TSM-310 PD14 | -0.33% | 310 | 45.5 | 37 | 8.38 | 20
Yingli 245W | YL245P-29b | -0.33% | 245 | 37.8 | 30.2 | 8.11 | 20
Yingli 285W | YL295P-35b | -0.33% | 285 | 45 | 35.5 | 8.02 | 20
Yingli 290W | YL295P-35b | -0.33% | 290 | 45.3 | 35.8 | 8.1 | 20
Yingli 295W | YL295P-35b | -0.33% | 295 | 45.4 | 36.3 | 8.12 | 20
Yingli 300W | YL295P-35b | -0.33% | 300 | 46.3 | 36.7 | 8.17 | 20
Yingli 305W | YL295P-35b | -0.33% | 305 | 46.3 | 37 | 8.25 | 20
Note on H1: Usually difference between Normal Cell Operating Temperature (NOCT) and STC temperature

## Rough Site Stringing Calculator
8000
Rough Site Stringing Calculator | [7 empty] | 5750
For a given number of modules and inverters, how many strings, of what lengths, will I have?
HiQ String Sizing
# Modules | 114
Wattage | 300
# Inverters | 3
AC Rating | 8000 |  | <--- Less Inverters |  | 3 | More Inverters --->
Strings | 6 |  | 1 | 2 |  | 4 | 5
|  | DC kW | 34200 | 34200 | 34200 | 34200 | 34200
# Strings | Length | AC kW | 8000 | 16000 | 24000 | 32000 | 40000
0 | 20 | DC/AC Ratio | 427.5% | 213.8% | 142.5% | 106.9% | 85.5%
6 | 19 |  | <----- Stacking Ratios ----->
Listed choices
User Input
Use at own risk, HiQ Solar, Inc. accepts no responsibility for errors, omissions, etc.
HiQ Solar, Inc. v4.1, Mar 2017
www.hiqsolar.com